## Sheet1
SR. NO. | DESCRIPTION OF WORK | Units | CHILLED WATER MANIFOLD (POST COOLING) | CHILLED WATER PIPING & INSULATION (POST COOLING) | CHILLED WATER MANIFOLD- (PRE COOLING) | CHILLED WATER PIPING & INSULATION- (PRE COOLING) | HOT WATER MANIFOLD | HOT WATER PIPING & INSULATION |  | LOW PRESSURE STEAM MANIFOLD | LOW PRESSURE STEAM PIPING & INSULATION | TOTAL | Remarks
A | manifold will be duly insulated with Nitrile Rubber with GC cloth insulation (Factory laminated GC cloth shall be green colour with 7 mils/200 GSM) of thickness as per the piping insulation thickness to avoid moisture condensation. | [11 empty] | FM Approved Color GC Face Nitrile rubber Insulation
1 | 300 mm dia | RMT |  | R.O. | [7 empty] | 0 | 38MM | rate for "0" to be Provided
2 | 250 mm dia | RMT |  | R.O. | [7 empty] | 0 | 32MM | rate for "0" to be Provided
3 | 200 mm dia | RMT |  | R.O. | [7 empty] | 0 | 32MM | rate for "0" to be Provided
4 | 150 mm dia | RMT |  | R.O. | [7 empty] | 0 | 32MM | rate for "0" to be Provided
5 | 125 mm dia | RMT |  | R.O. | [7 empty] | 0 | 32MM | rate for "0" to be Provided
6 | 100 mm dia (Manifold size typ) | RMT | 0 | R.O. | 12 | 10 | [5 empty] | 22 | 32MM
7 | 80 mm dia | RMT | 12 | 10 | 12 | 10 | [5 empty] | 44 | 32MM
8 | 65 mm dia | RMT | 72 | 60 | 24 | 20 | [5 empty] | 176 | 32MM
9 | 50 mm dia | RMT | 192 | 160 | 24 | 20 | [5 empty] | 396 | 32MM
10 | 40 mm dia | RMT | 96 | 80 | 24 | 20 | [5 empty] | 220 | 32MM
11 | 32 mm dia | RMT | 120 | 100 | 96 | 80 | [5 empty] | 396 | 32MM
12 | 25 mm dia | RMT | 12 | 10 | 84 | 70 | [5 empty] | 176 | 25MM
13 | 20 mm dia | RMT | 0 |  | R.O. | [6 empty] | 0 | 25MM | rate for "0" to be Provided
14 | 15 mm dia | RMT | [9 empty] | 0 | 25MM | rate for "0" to be Provided
B | manifold will be duly insulated with Nitrile Rubber with GC cloth insulation (Factory laminated GC cloth shall be green colour with 7 mils/200 GSM) of thickness as per the piping insulation thickness to avoid moisture condensation. | [11 empty] | FM Approved Color GC Face Nitrile rubber Insulation
1 | 250 mm dia | RMT | [9 empty] | 0 | 19MM | rate for "0" to be Provided
2 | 200 mm dia | RMT | [9 empty] | 0 | 19MM | rate for "0" to be Provided
3 | 150 mm dia | RMT | [9 empty] | 0 | 19MM | rate for "0" to be Provided
4 | 125 mm dia | RMT | [9 empty] | 0 | 19MM | rate for "0" to be Provided
5 | 100 mm dia (Manifold size typ) | RMT | [9 empty] | 0 | 19MM | rate for "0" to be Provided
6 | 80 mm dia | RMT | [9 empty] | 0 | 13MM | rate for "0" to be Provided
7 | 65 mm dia | RMT | [9 empty] | 0 | 13MM | rate for "0" to be Provided
8 | 50 mm dia | RMT |  |  |  |  | 0 |  |  |  |  | 0 | 13MM | rate for "0" to be Provided
9 | 40 mm dia | RMT |  |  |  |  | 72 | 60 |  |  |  | 132 | 13MM
10 | 32 mm dia | RMT |  |  |  |  | 36 | 30 |  |  |  | 66 | 13MM
11 | 25 mm dia | RMT |  |  |  |  | 120 | 100 |  |  |  | 220 | 13MM
12 | 20 mm dia | RMT |  |  |  |  | 0 | 0 |  |  |  | 0 | 13MM | rate for "0" to be Provided
13 | 15 mm dia | RMT | [9 empty] | 0 | 13MM | rate for "0" to be Provided
B | Drain piping - UPVC For Chilled water (Pre & Post Cooling)
| Supply, installation, testing & commissioning of schedule 40 UPVC drain piping complete with fittings, U traps, support Connection to Main Hadder & class "O" elastomeric Nitrile Rubber insulation tubes of 13 mm thickness of width as specified for following sizes: | [11 empty] | FM Approved Black GC Face Nitrile rubber Insulation
1 | 100 mm dia | RMT | 100 | [8 empty] | 100 | 13mm
2 | 80 mm dia | RMT | 100 | [8 empty] | 100 | 13mm
3 | 65 mm dia | RMT | 30 | [8 empty] | 30 | 13mm
4 | 50 mm dia | RMT | 75 | [8 empty] | 75 | 13mm
5 | 40 mm dia | RMT | 210 | [8 empty] | 210 | 13mm
6 | 32 mm dia | RMT | 50 | [8 empty] | 50 | 13mm
C | LOW PRESSURE STEAM MANIFOLD
| Supply and installation of Thermal insulation over low pressure steam coil manifolds with Light resin bonded mattresses of Rock Wool/mineral wool as per IS:8183 (part 3) with density of not less than 100 Kg/m3, Thermal Conductivity at 0.034 W/m°K at 25°C mean temperature. Finishing shall be with 22 SWG, 99 % Pure Aluminum Sheets. The cladding shall be fixed with Aluminum band / SS 304 band size ¾” X 24 SWG at a distance of 450mm center to center. | [11 empty] | Rock Wool/mineral wool as per IS:8183 (part 3) with density of not less than 100 Kg/m3,
1 | 50 mm dia (Manifold size typ) | RMT | [9 empty] | 0 | 50mm | rate for "0" to be Provided
2 | 40 mm dia | RMT | [9 empty] | 0 | 50mm | rate for "0" to be Provided
3 | 32 mm dia | RMT | [9 empty] | 0 | 50mm | rate for "0" to be Provided
4 | 25 mm dia | RMT | [6 empty] | 120 | 200 |  | 320 | 50mm
5 | 20 mm dia | RMT | [9 empty] | 0 | 50mm | rate for "0" to be Provided
D.2 | INDOOR INSULATION FOR DUCTING
INSULATION MATERIAL SHALL BE FM APPROVED.
PLAIN NITRILE RUBBER INSULATION FOR DUCTING
D.2.1 | Supply, installation, testing & commissioning of plain class "O" elastomeric nitrile Rubber for ducting. Insulation to be provided complete for fittings, adhesive (elbows, taper, flanges etc.) etc all as per specifications. (Indoor Insulation) | [11 empty] | FM Approved Plain Nitrile rubber Insulation
D.2.1.1 | 25 mm thickness | sq.m | [9 empty] | R.O. |  | rate for "R0" to be Provided
D.2.1.2 | 13 mm thickness | sq.m | [9 empty] | R.O. |  | rate for "R0" to be Provided
NITRILE RUBBER INSULATION WITH GC CLOTH WITH COLOUR FOR DUCTING
D.2.2 | Supply, installation, testing & commissioning of plain class "O" elastomeric nitrile Rubber with GC cloth (GC cloth shall be with 7 mils/200 GSM) with colour for ducting. Insulation to be provided complete for fittings, adhesive (elbows, taper, flanges etc.) etc all as per specifications. (Indoor Insulation) | [11 empty] | FM Approved Color GC Face Nitrile rubber Insulation
Colour shall be decided in coordination with client / consultant
D.2.2.1 | 25 mm thickness | sq.m | [9 empty] | R.O. |  | rate for "R0" to be Provided
D.2.2.2 | 13 mm thickness | sq.m | [9 empty] | R.O. |  | rate for "R0" to be Provided
NITRILE RUBBER INSULATION WITH Al FOIL FOR DUCTING
D.2.3 | Supply, installation, testing & commissioning of Class "O" elastomeric nitrile Rubber with factory laminated Aluminum foil for ducting. Insulation to be provided complete for fittings, adhesive (elbows, taper, flanges etc.) etc all as per specifications. ( Indoor Insulation ) | [11 empty] | FM Approved Al Foil Face Nitrile rubber Insulation
D.2.3.1 | 32 mm thickness | sq.m | [9 empty] | R.O. |  | rate for "R0" to be Provided
D.2.3.2 | 13 mm thickness | sq.m | [9 empty] | R.O. |  | rate for "R0" to be Provided
XLPE INSULATION FOR DUCTING
D.2.4 | Supply, installation, testing & commissioning of Class "O" chemically crosslinked polyethylene with factory backed alupet foil, FM approved, for ducting. Insulation to be provided complete for fittings, adhesive (elbows, taper, flanges etc.) etc all as per specifications. ( Indoor Insulation ) | [11 empty] | FM Approved Alupet Foil Face XLPE Insulation
D.2.4.1 | 25 mm thickness | sq.m | [9 empty] | 2240
D.2.4.2 | 19 mm thickness | sq.m | [9 empty] | 2000
D.2.4.3 | 13 mm thickness | sq.m | [9 empty] | 4240
Note: Supply air and return air duct flanges shall be provided with 150mm width of duct insulation having same thickness as supply air and return air insulation. NO SEPARATE MEASUREMENT SHALL BE PROVIDED FOR THIS.
D.16 | UNDERDECK INSULATION.
| Underdeck Insulation with 25 mm thick class 'O' elastomeric nitrile rubber insulation of 40 - 60kg/m3 density wherever roof is exposed to sun and the area is airconditioned as per specification | sq.m | [9 empty] | R.O. |  | rate for "R0" to be Provided