## Sheet1
SL.NO. | PARTICULARS | UNITS | Total qty | UNIT RATE SUPPLY (Rs.) |  | Total Supply Amount | UNIT RATE E & C (Rs.) |  | Total E&C Amount (Including Taxes) | Total
|  |  |  | Supply Rate [Basic + P&F + Transport + Transit Insurance + Octroi, if | Taxes (GST) (Indicate % here) |  | E & C Rate (Basic) | Taxes (GST) (Indicate % here) |  |  | Compliance
1)The scope include
a) Supply shall be on FOR Site basis, including packing & forwarding, loading, frieght, transit insurance (covering unloading as well) etc
b) Scope of Testing and Commissioning shall also include Unloading, Storage & Handling, Watch and Ward and handing over along with necessary documentations as required by Client/PMC
2) In case of any conflict between Technical Specifications and BOQ, the BOQ sheest from layouts shall prevail over the other.
3) As far as possible vendor should plan for bulk procurement of the materials so as to place order directly to primary manufacturers.
4) BOQ shall be followed for method of measurement. In case BOQ is silent, technical specification will be referred.
5) Unless otherwise specified, measurement shall be only for actual laid/installed quantity as per the approved drawing. Wastages/breakages (if any) shall not be considered for measurement and consequent payment.
6)The contractor is requested to provide equipment selections as per the specified capacities.
7)The provided pump heads are preliminary; the contractor should perform detailed head loss calculations based on the actual piping layout and submit for approval.
8) The provided fan static pressures are preliminary; the contractor should conduct a detailed duct pressure loss calculation and submit the fan selection for approval.
SECTION B | LOW SIDE WORK-WATER SIDE
1 | LOW HOT WATER, LOW CHILLED WATER & MEDIUM CHILLED WATER PIPING
Supply, installation, testing, and commissioning of piping system including: For DN ≤ 200: Hot-dip galvanized welded steel pipes For DN ≥ 250: Spiral welded steel pipes (SW) Pipes shall conform to IS:1239 / IS:3589 / ASTM A53 or other relevant applicable standards, medium/heavy class. Scope shall include all required pipe fittings and accessories such as elbows, tees, reducers, caps, flanges, couplings, unions, gaskets, bolting materials, etc., with: DN < 50: Threaded (screw) connections DN ≥ 50: Welded connections Pipes shall be hot-dip galvanized internally and externally after fabrication with a minimum zinc coating of 85 microns, in compliance with IS:4759 / ASTM A123. The rate shall include all necessary supports such as clamps, hangers, U-clamps, PUF insulated saddles (PUF gutti), wire rope hanger systems, etc., installed at max 2.0 m spacing or as per PMS/structural design requirements. The item shall also include all civil/mechanical works such as excavation, backfilling (if applicable), core cutting, wall chasing, etc., for proper alignment and installation. All pipelines shall be pressure tested to specification and approved by the Engineer-in-Charge. Note: Rate shall be inclusive of all materials, labor, consumables, tools & tackles, transportation, testing, commissioning, and all incidental works required to complete the system as per Tender Technical Specifications and PMS.
| Supply and installation of thermal insulation for chilled water pipelines installed on the terrace and inside shafts using flame-retardant closed-cell B-type PVC/NBR rubber-based elastomeric insulation shells (FM approved), with factory-applied 24G aluminum cladding for UV protection and mechanical durability. Insulation shall be installed using the manufacturer-recommended adhesive, with VOC content not exceeding 850 g/L. The insulation material shall comply with the following performance and environmental criteria: Fire Performance: Conforms to IS 15061, IS 16406, and IS 3808, ensuring:Low flammability (self-extinguishing), Medium smoke generation, No flaming droplet formation, Stable under brief thermal exposure. Thermal Conductivity: ≤ 0.034 W/m·K at 20°C ≤ 0.037 W/m·K at 40°C (Tested as per EN 12667 / EN ISO 8497) Water Vapor Permeability: Water Vapor Diffusion Resistance Factor (μ) > 1,000 (As per EN 12086 / EN 13469) Water Absorption: < 0.2% by volume (As per ASTM C1763 / ASTM C209) Environmental & Safety Compliance: • EPD compliant • CFC and HCFC free • Dust-free and fiber-free composition Thickness of insulation shall be provided as per Tender specifications and installed using proper sealing, clamping, and protection measures to prevent condensation and heat loss. The scope shall include all fittings, bends, joints, valves, and supports along the insulated piping, ensuring a continuous vapor barrier and professional finish, in line with the manufacturer’s guidelines and project specifications | [9 empty] | Comply
1.1 | DN 1100 mm | Rmt. | 320
1.2 | DN 900 mm | Rmt. | 20
1.3 | DN 800 mm | Rmt. | 150
1.4 | DN 700 mm | Rmt. | 450
1.5 | DN 650 mm | Rmt. | 310
1.6 | DN 600 mm | Rmt. | 330
1.7 | DN 550 mm | Rmt. | 500
1.8 | DN 500 mm | Rmt. | 820
1.9 | DN 450 mm | Rmt. | 680
1.1 | DN 400 mm | Rmt. | 1040
1.11 | DN 350 mm | Rmt. | 1000
1.12 | DN 300 mm | Rmt. | 600
1.13 | DN 250 mm | Rmt. | 820
1.14 | DN 200 mm | Rmt. | 2210
1.15 | DN 150 mm | Rmt. | 970
1.16 | DN 125 mm | Rmt. | 1400
1.17 | DN 100mm | Rmt. | 1990
1.18 | DN 80mm | Rmt. | 2590
1.19 | DN 65mm | Rmt. | 670
1.2 | DN 50mm | Rmt. | 1780
1.21 | DN 40mm | Rmt. | 370
1.22 | DN 32mm | Rmt. | 510
3 | CONDENSER WATER PIPING WITHOUT INSULATION
Supply, installation, testing, and commissioning of piping system including: For DN ≤ 200: Hot-dip galvanized welded steel pipes For DN ≥ 250: Spiral welded steel pipes (SW) Pipes shall conform to IS:1239 / IS:3589 / ASTM A53 or other relevant applicable standards, medium/heavy class. Scope shall include all required pipe fittings and accessories such as elbows, tees, reducers, caps, flanges, couplings, unions, gaskets, bolting materials, etc., with: DN < 50: Threaded (screw) connections DN ≥ 50: Welded connections Pipes shall be hot-dip galvanized internally and externally after fabrication with a minimum zinc coating of 85 microns, in compliance with IS:4759 / ASTM A123. The rate shall include all necessary supports such as clamps, hangers, U-clamps, PUF insulated saddles (PUF gutti), wire rope hanger systems, etc., installed at max 2.0 m spacing or as per PMS/structural design requirements. The item shall also include all civil/mechanical works such as excavation, backfilling (if applicable), core cutting, wall chasing, etc., for proper alignment and installation. All pipelines shall be pressure tested to specification and approved by the Engineer-in-Charge. Note: Rate shall be inclusive of all materials, labor, consumables, tools & tackles, transportation, testing, commissioning, and all incidental works required to complete the system as per Tender Technical Specifications and PMS.
The rate quoted shall inlude the cost of hot dipped MS supports at required heights and the supports shall be treated with 2 quotes of redoixide and apporoved paint , pipe running shall be supported at a height of minimum 1 mtrs from the terrace Floor level for easy access and Terrace cleaning
Exposed Pipe shall be treated with FRP coat to the thickness of 2 mm using 300 gsm Chopped strand mat applied to the Pipeline with the help of Activated Polyester Resin with approved shade of Colour.
Unexposed pipe shall be treated with 2 coats of primer & 2 coats of paint of approved shade and colour.
1.1 | DN 1500 mm | Nos | 220
1.2 | DN 600 mm | Nos | 110
1.3 | DN 500 mm | Nos | 40
1.4 | DN 450 mm | Nos | 260
1.5 | DN 400 mm | Nos | 1010
1.6 | DN 300 mm | Nos | 90
1.7 | DN 200 mm | Nos | 1170
5 | PROCESS WATER PIPING(PCW)
Supply, Installation, Testing, Commissioning, and Handing Over of Stainless Steel Piping System (Process Cooling Water) conforming to ASTM A312 Gr. TP304 (SUS304) with dimensional standard ANSI B36.19, joined using argon arc welding (TIG), suitable for process cooling water system. The scope includes: Pipes, fittings (elbows, tees, reducers, flanges, couplings), gaskets, bolts, and all accessories. Installation in open ceiling with aluminum foil cladding for exposed sections. Buried pipe sections with three-oil two-cloth anticorrosion protection. Complete support system including clamps, hangers, guides, vibration isolators, etc. All related civil/mechanical works including alignment, flushing, hydrotesting, and other associated works. As per PMS attached in Section D and relevant tender specifications. Note: Rate shall be inclusive of all materials, labor, consumables, tools, tackles, equipment, transportation, and any incidental works to complete the job in all respects.
| Supply & fixing of Thermal Insulation for process cooling water pipes running at terrace & inside the shaft using Class " 0 " Closed cell nitrile rubber elastomeric foam insulation laminated with 24G aluminium Cladding recommended adhesive where the VOC level should not exceed more than 850 grams / Litre. Insulation material manufactured should have fire properties - Class 0 Rating as per BS 476 Part 7 & Part 6 test & HB and V0 Rating as per UL 94. Insulation shall have a minimum Thermal Conductivty of 0.037 W / m K @ 20 Deg C as per EN 12667/ EN ISO 8497. Insulation shall have a Water Vapor Diffusion Resistance Factor of 7,000 as per EN 12086 / EN 13469. Insulation shall not absorb water more than 0.2% by volume as per ASTM C 1763 / ASTM C 209. Insulation material shall be EPD Compliant and CFC HCFC Free. Insulation shall be Dust and Fibre Free. | [9 empty] | Comply
5.1 | DN 400 mm | Nos | 20
5.2 | DN 350 mm | Nos | 30
5.3 | DN 300 mm | Nos | 330
5.4 | DN 250 mm | Nos | 180
5.5 | DN 200 mm | Nos | 400
5.6 | DN 150 mm | Nos | 350
5.7 | DN 100 mm | Nos | 590
5.8 | DN 80 mm | Nos | 70
5.9 | DN 65 mm | Nos | 60
5.1 | DN 50 mm | Nos | 600
5.11 | DN 40 mm | Nos | 40
5.12 | DN 32 mm | Nos | 220
18 | THERMAL INSULATION
| Supply & fixing of Thermal Insulation for ducting application using Class " 0 " Closed cell nitrile rubber elastomeric foam insulation laminated with chemically treated glass cloth of 7 mil / 0.18 mm thickness Thermal conductivity of insulation material shall not exceed 0.036 W/(m.K) at mean temperature of 24C as per ASTM C 518 / ASTM C 177. The insulation material shall have water absorption of 0.2% by volume as per ASTM C 1763 ,shall have fire performance rating of 25/50 as per ASTM E 84. Density will be 40 to 60 Kg/m3 .• The insulation material shall have Microban®* an anti-microbial product, which is EPA (Environmental Protection Agency), USA Approved, as an integral part of insulation that cannot be washed off or worn off.The insulation material shall give enhanced level of protection against harmful Microbes such as fungi and mold and should confirm to ASTM G 21, UL 181 & ASTM E 2180. Water Vapor Permeability of insulation material shall be minimum 0.05 Perm-inch. without any external barrier as per ASTM E 96 Procedure A. The ductseal adhesives for the application of insulation should be of principal manufacturer. Application services to be availed from the principal insulation company and detailed report to be provided by the insulation manufacturer after installation | [9 empty] | Comply
18.1 | 32 mm thick for Supply air ducts | SQM | 14475
18.2 | 25 mm thick for Return air ducts | SQM | 4540
19 | ACCOUSTIC INSULATION
| Supply, Installation, Testing and Commissioning of DUCT acoustic insulation- :Supply & fixing of Acoustic insulation for Supply air duct using 10 mm thick class 1 rating Open cell nitrile rubber elastomeric insulation with density of 140 - 180 kg / m³. The insulation manafactured as per BS 476 Part 7 & which should also meet UL 94test supplementary materials for air distribution system which should not absorbs less 0.2% water by volume (ASTM c 209), should not support microbial growth (ASTM 2180, G21, G22) and should not emit objectionable odors (ASTM C 665) and should have thermal conductivity of 0.04W/m K @ 20 degC as per DIN EN 12667. and water vapor permeance of 0.10. Adhesive shall be used additionally with VOC level not exceeding 50 grms / Litre. Method of measurement:- Acoustic insulation shall be measured on the basis of ducting surface area based on the portion of duct to be acoustically lined, the area before insulation shall be measured and paid for. | sqm | 5302 | [7 empty] | Comply with deviation k value is 0.047 W/mk, it not affect acoustic property of material