## Sheet1 (hidden)
PROJECT:- ARFF-MEDICAL FACILITY @ SARDAR VALLABH BHAI INTERNATIONAL ADANI AIRPORT AHMEDABAD
S. No. | DESCRIPTION | Unit | QTY
INSULATION
1 | THERMAL INSULATION FOR DUCT
| Supplying and fixing of following thickness closed cell Nitrile rubber (Class "O") insulation on existing duct after applying suitable adhesive for Nitrile rubber. The joints shall be sealed with 50 mm wide and 3 mm thick self adhesive nitrile rubber tape insulation complete as per specifications and as required. |  |  | Armaflex/ ALP Aeroflex / K-Flex
Thermal insulation material for Duct insulation shall be Closed Cell Nitrile Rubber insulation. Thermal conductivity as per IS/ DIN EN 12667 / EN ISO8497 of the insulation material shall not exceed 0.038 W/moK or 0.212 BTU / (Hr-ft2-oF/inch) at an average temperature of 30oC. Density of the nitrile rubber shall be 40-60 Kg/m3, The product shall have temperature range of -400C to +1050C as per EN 14706, EN 14707 and EN 14304. The insulation material shall be fire rated for Class 0 as per BS 476 Part 6 : 1989 for fire propagation test and for Class 1 as per BS 476 Part 7, 1987 for surface spread of flame test. The material also pass UL 94 Test for Vertical Burning and Horizontal Burning and FM Approved. Water vapour permeability shall be not less than 0.024 per inch (2.48 x 10-13 Kg/m.s.Pa i.e. µ>7000: Water vapour diffusion resistance) as per IS/ EN 12086 & EN13469.
1.1 | 19 mm | SQM. | 285
2 | DUCT ACOUSTIC LINING
Supplying and fixing of following thickness of Acoustic Insulation Inside the Duct with Nitrile Rubber open cell foam with Density 140 - 180 Kg/m3 & shall be fibre free. The material shall have a thermal conductivity not exceeding 0.047 W/m.K @ 20 Deg. C & shall conform to Class 1 rating for surface spread of Flame in accordance to BS 476 Part 7. The insulation shall pass Air Erosion Resistance Test in accordance to ASTM Standard C 1071-05 (section 12.7), from an independent testing agency & should have built-in Ultra-Fresh Anti-Microbial Protection, and should pass Fungi Resistance as per ASTM G21 & Bacterial resistance as per ASTM 2180. To be applied using Adhesive
2.1 | 15mm | SQM. | 55
3 | UNDERDECK INSULATION
| Supply & fixing of Physically / Chemically crosslinked polyethylene foam for the roofing underdeck insulation, with factory reinforced alupet foil facing with flange at both side for joints, having Class O fire properties and very low fire propagation of < 5.5, passing E-84 at < 25/50,the density of the foam should be not less than 25-30kg/m3 and the maximum thermal conductivity K should be 0.032W/mK @23 Deg C, the permeability resistance factor u shouldn't be less than 14000. Underdeck Insulation shall be anti microbial and anti fungal as per ASTM G 21 and ASTM E2180. Insulation material should be CFC & HCFC free (proved by test report issued by accredited lab). | SQM. | 425
6 | COPPER REFRIGERANT PIPING WITH INSULATION
Supply, Installation, testing and commissioning including vaccumization and Nitrogen testing of following nominal sizes of soft/hard drawn copper refrigerant piping for VRV/VRF system, complete with fittings, with suitable adjustable ring type hanger supports, jointing/brazing including accessories, insulated with Class-O closed cell elastometric nitrile rubber tubular sleeves sections of specified thickness (with mechanical protection of aluminium cladding of 26 Gauge at outdoor locations) as given below for Suction and Liquid lines, all accessories as per specifications etc. as required :
Piping vaccumiazation and Nitrogen testing to be done by contractor and price for the same to be included
Thickness of pipes should be as per VRF manufacturer's recommendation.
6.1 | 34.9 mm dia with 19mm thick insulation | Mtrs. | 50
6.2 | 31.8 mm dia with 19mm thick insulation | Mtrs. | 5
6.3 | 28.6 mm dia with 19mm thick insulation | Mtrs. | 15
6.4 | 25.4 mm dia with 19mm thick insulation | Mtrs. | 5
6.5 | 22.2 mm dia with 19mm thick insulation | Mtrs. | 40
6.6 | 19.1 mm dia with 13mm thick insulation | Mtrs. | 30
6.7 | 15.9 mm dia with 13mm thick insulation | Mtrs. | 55
6.8 | 12.7 mm dia with 13mm thick insulation | Mtrs. | 20
6.9 | 9.5 mm dia with 13mm thick insulation | Mtrs. | 55
6.1 | 6.4 mm dia with 13mm thick insulation | Mtrs. | 20

## Sheet2
PROJECT:- ARFF-MEDICAL FACILITY @ SARDAR VALLABH BHAI INTERNATIONAL ADANI AIRPORT AHMEDABAD
S. No. | DESCRIPTION | Unit | QTY | Make
SUB-HEAD 'D' - INSULATION
1 | THERMAL INSULATION FOR DUCT |  |  | Armaflex/ ALP Aeroflex / K-Flex
Supplying and fixing of following thickness closed cell Nitrile rubber (Class "O") insulation on existing duct after applying suitable adhesive for Nitrile rubber. The joints shall be sealed with 50 mm wide and 3 mm thick self adhesive nitrile rubber tape insulation complete as per specifications and as required.
Thermal insulation material for Duct insulation shall be Closed Cell Nitrile Rubber insulation. Thermal conductivity as per IS/ DIN EN 12667 / EN ISO8497 of the insulation material shall not exceed 0.038 W/moK or 0.212 BTU / (Hr-ft2-oF/inch) at an average temperature of 30oC. Density of the nitrile rubber shall be 40-60 Kg/m3, The product shall have temperature range of -400C to +1050C as per EN 14706, EN 14707 and EN 14304. The insulation material shall be fire rated for Class 0 as per BS 476 Part 6 : 1989 for fire propagation test and for Class 1 as per BS 476 Part 7, 1987 for surface spread of flame test. The material also pass UL 94 Test for Vertical Burning and Horizontal Burning and FM Approved. Water vapour permeability shall be not less than 0.024 per inch (2.48 x 10-13 Kg/m.s.Pa i.e. µ>7000: Water vapour diffusion resistance) as per IS/ EN 12086 & EN13469.
1.1 | 19 mm | SQM. | 135
2 | DUCT ACOUSTIC LINING
Supplying and fixing of following thickness of Acoustic Insulation Inside the Duct with Nitrile Rubber open cell foam with Density 140 - 180 Kg/m3 & shall be fibre free. The material shall have a thermal conductivity not exceeding 0.047 W/m.K @ 20 Deg. C & shall conform to Class 1 rating for surface spread of Flame in accordance to BS 476 Part 7. The insulation shall pass Air Erosion Resistance Test in accordance to ASTM Standard C 1071-05 (section 12.7), from an independent testing agency & should have built-in Ultra-Fresh Anti-Microbial Protection, and should pass Fungi Resistance as per ASTM G21 & Bacterial resistance as per ASTM 2180. To be applied using Adhesive
2.1 | 15mm | SQM. | 55
3 | UNDERDECK INSULATION
| Supply & fixing of Physically / Chemically crosslinked polyethylene foam for the roofing underdeck insulation, with factory reinforced alupet foil facing with flange at both side for joints, having Class O fire properties and very low fire propagation of < 5.5, passing E-84 at < 25/50,the density of the foam should be not less than 25-30kg/m3 and the maximum thermal conductivity K should be 0.032W/mK @23 Deg C, the permeability resistance factor u shouldn't be less than 14000. Underdeck Insulation shall be anti microbial and anti fungal as per ASTM G 21 and ASTM E2180. Insulation material should be CFC & HCFC free (proved by test report issued by accredited lab). | SQM. | 380
8 | COPPER REFRIGERANT PIPING WITH INSULATION
Supply, Installation, testing and commissioning including vaccumization and Nitrogen testing of following nominal sizes of soft/hard drawn copper refrigerant piping for VRV/VRF system, complete with fittings, with suitable adjustable ring type hanger supports, jointing/brazing including accessories, insulated with Class-O closed cell elastometric nitrile rubber tubular sleeves sections of specified thickness (with mechanical protection of aluminium cladding of 26 Gauge at outdoor locations) as given below for Suction and Liquid lines, all accessories as per specifications etc. as required :
Piping vaccumiazation and Nitrogen testing to be done by contractor and price for the same to be included
Thickness of pipes should be as per VRF manufacturer's recommendation.
7.1 | 34.9 mm dia with 19mm thick insulation | Mtrs. | RO
7.2 | 31.8 mm dia with 19mm thick insulation | Mtrs. | RO
7.3 | 28.6 mm dia with 19mm thick insulation | Mtrs. | 20
7.4 | 25.4 mm dia with 19mm thick insulation | Mtrs. | 10
7.5 | 22.2 mm dia with 19mm thick insulation | Mtrs. | 50
7.6 | 19.1 mm dia with 13mm thick insulation | Mtrs. | 30
7.7 | 15.9 mm dia with 13mm thick insulation | Mtrs. | 55
7.8 | 12.7 mm dia with 13mm thick insulation | Mtrs. | 45
7.9 | 9.5 mm dia with 13mm thick insulation | Mtrs. | 55
7.1 | 6.4 mm dia with 13mm thick insulation | Mtrs. | 20
8 | Drain Piping
Providing & fixing of heavy duty uPVC Pipe complete with fittings, supports as per specifications and duly insulated with 9mm thickness of closed cell tubular nitrile rubber as required & as per specifications.
8.1 | 40 mm dia with 9 mm thick insulation | Mtrs. | RO
8.2 | 32 mm dia with 9 mm thick insulation | Mtrs. | 40
8.3 | 25 mm dia with 9 mm thick insulation | Mtrs. | 30