## Sheet1
Sr. No. | Description | Unit | Tender Specification | Vendor confirmation
2 | DUCT INSULATION
2.1 | Type |  | Chemically Class "O" crosslinked polyethylene with factory backed alupet foil
2.2 | Thermal conductivity | W/mᵒK | not more than 0.035 w/mᵒK at 0ᵒC and suitable for a service temperature of - 40 ᵒC to 105ᵒC
2.3 | Density | kg/m3 | 40 to 60 kg/m3
2.4 | Thickness supply duct | mm | 25mm
2.5 | Thickness supply duct | mm | 19mm
2.6 | Thickness return duct | mm | 13mm
3 | INSULATION ON PIPE
3.1 | Type |  | Elastomeric sheet of class “O” Nitrile rubber
3.2 | Thermal conductivity | w/mᵒK | not more than 0.035 w/mᵒK at 0ᵒC and suitable for a service temperature of - 40 ᵒC to 105ᵒC
3.3 | Density | kg/m3 | 40 t0 60 kg/m3
3.4 | Thickness | mm