## INSULATION

  - Scope:

The scope of work comprises the supply, installation, testing & commissioning & document of Insulation along with its accessories for M/s Zydus Animal Health and Investments Ltd.  The specifications shall be read in conjunction with bill of quantities.

  - Objective:

The purpose of this document is to specify the requirements of Hot & Cold Insulation and to covers information about its accessories.

  - Specification

  - Description:

The scope of work covers thermal insulation for:

i)	Cold Insulation 1) 	 Pipes

2)          Ducts

3)          Equipment’s

ii)	Hot Insulation	  1)	 Pipes

2)          Ducts

3)          Equipment’s

4)          Exhaust flues (if any)

  - Material:

Following materials shall be used:

i)  Cold Insulation	1)Fire inhibiting expanded polystyrene rigid section 18kg/cum thermal conductivity of not more than 0.03 w/m ᵒC at 10 deg C mean temperature. (Not applicable)

2) Duct - Elastomeric sheet of class “O” self-extinguishing CFC free with a thermal conductivity of not more than 0.035 w/mᵒK at 0ᵒC and suitable for a service temperature of - 40 ᵒC to 105 C. The density of rubber shall be minimum 60 kg/M³ and water vapour diffusion resistance should not be more than 4000. The material should be CFC free and UV resistant.

Piping - Elastomeric sheet / tubing (Nitrile Rubber) of class “O” self-extinguishing CFC free with a thermal conductivity of not more than 0.035 w/mᵒK at 0ᵒC and suitable for a service temperature of - 40 ᵒC to 105 C with factory installed glass cloth.

3)  Close cell cross- linked Polyethylene Foam sheet of Class “O” fire rating as per DIN 4102 with factory baked Aluminium foil faced, self-extinguishing with a thermal conductivity of not more than 0.032 w/mᵒK at 0ᵒC and density shall be 30+/- 10% as per DIN 53420 .

4) Resin bonded fiberglass having K value not more than 0.032 and density not less than 24 kg/cu. m. (Not applicable)

ii)  Hot Insulation	1) Elastomeric tubing (Nitrile rubber) of class “O”                                                        self-extinguishing CFC free with a thermal conductivity of not more than 0.03 w/mᵒK at 0 ᵒC and suitable for service temperature of -40 ᵒC to 105 ᵒC.

2) Resin bonded rock wool confirming to ASTM C592 class II for blanket and ASTM C547 class III for preformed pipe section having density more than 96 kg/m3 and thermal conductivity not more than 0.05 mW/cm°C at 100 deg C mean temperature and with one side wire netting of size 24G x 20. The material shall be suitable for intended operational temperature range from ambient to 550°C (Only for hot water) (Not applicable)

  - Duct Insulation:

Duct located INDOOR / OUTDOOR spaces shall be insulated to the following thickness.

| Location | Cross linked Polyethylene with factory baked Al foil | Elastomeric Sheet (Nitrile) plain / with GC cloth | Elastomeric Sheet (Nitrile) with Al foil |
| --- | --- | --- | --- |
| Non A/C spaces - Cold supply duct Cold return duct | 25 mm 15 mm | 25 mm 13 mm | 32 mm 13 mm |
| Air conditioned spaces Cold Supply duct Return duct | 25 mm 15 mm | 25 mm 13 mm | 32 mm 13 mm |

** Thickness mentioned in BOQ shall be treated as Final **

Indoor insulation shall be applied as follows (For EPS):

Clean the duct surface & apply a coat of bituminous paint. Apply hot bitumen 80/25 @ 1.5 kg/sqm    on the surface and the inner side of insulation material.

Stick insulation slabs & hold at 1000mm centre with PVC Strapping & blind the surface with hot bitumen at 1.5 kg/sq. m. Seal the joints with approved sealant or hot bitumen.

Wrap 10 mil glass cloths with PVC strapping at 1000mm spacing & seal with hot bitumen / Aluminium foil of 42 Gauge with 50 mm overlap and seal all joints using BOPP tape of Wonder / 3M make.

Indoor insulation shall be applied as follows (For Nitrile / Polyethylene):

- Clean the duct surface thoroughly & apply a coat of  adhesive recommended by the manufacturer on the duct as well as on sheet and allow it to cure (Self-adhesive sheet can also be used )

- Stick insulation slabs with pre-laminated aluminium foil of minimum 30 micron on duct uniformly. Seal the joints with approved self-adhesive Aluminium tape of same material.

- Flanges or any other exposed portion should be covered with 50 mm wide insulation slab of same material having same thickness.

Outdoor insulation shall be applied as follows (For EPS):

- Clean the duct surface & apply a coat of bituminous paint. Apply hot bitumen 80/25 @ 1.5 kg/sqm on the surface and the inner side of insulation material.

- Stick insulation slabs & hold at 1000mm centre with 24G galvanized steel wire or PVC strapping & blind the surface with hot bitumen at 1.5 kg/sqm. Seal the joints with approved sealant.

- Wrap 10 mil glass cloth / 500 micron polythene sheet & seal with hot bitumen.

- Clad the duct with 0.5mm thick Al sheet with 50mm overlap and fixed with self-tapping no. 8 sheet metal screw and seal with mastic sealant.

Outdoor insulation shall be applied as follows (For Nitrile/ Polyethylene):

- Clean the duct surface thoroughly & apply a coat of adhesive recommended by the manufacturer on the duct as well as on sheet and allow it to cure. (Self-adhesive sheet can also be used)

- Stick insulation slabs with/ without pre-laminated aluminium foil (as specified in BOQ) on duct uniformly. Seal the joints with approved self-adhesive Aluminium tape.

- Flanges or any other exposed portion should be covered with 50 mm wide insulation slab of same material and thickness.

- If insulation slab is without Aluminium foil then clad the duct with 0.5mm thick Al sheet with 50mm overlap and fixed with self-tapping no. 8 sheet metal screw and seal with mastic sealant.

  - Pipe Insulation

i) Cold Insulation

Cold pipe insulation shall be selected as follows:

| Application | Minimum Thickness (mm) | Layer (No.) | Pipe (mm dia) | Material |
| --- | --- | --- | --- | --- |
| Chilled water supply & return (6°C) | 25 32 38 (19mm + 19mm) | One up to 250 mm | Up to 25 mm 32-250 Above 250 | Plain Nitrile rubber / Nitrile rubber with GC cloth |
|  | 25 30 35 | One | 10-40 50-150 Above 150 | Cross linked Polyethylene |
| Hot water supply & return (50°C) | 13 19 | One | Up to 80 mm Above 80 mm | Plain Nitrile rubber / Nitrile rubber with GC cloth |
| Drain Piping | 32 | One | All pipe sizes | Plain Nitrile rubber / Nitrile rubber with GC cloth |

Indoor Insulation (For EPS):

- Clean the duct surface & apply a coat of bituminous paint. Apply hot bitumen 80/25 @ 1.5 kg/sq. m on the surface and the inner side of insulation material.

- Stick insulation slabs & hold at 1000mm centre with 24G galvanised steel wire or PVC strapping & blind the surface with hot bitumen at 1.5 kg/sq. m. Seal the joints with approved sealant.

- Clad the surface with 0.5mm thick Al sheet with 50mm overlap and fixed with self-tapping no. 8 sheet metal screw and seal with mastic sealant.

Indoor insulation shall be applied as follows (For Nitrile/ Polyethylene):

- Clean the pipe surface thoroughly & apply a coat of adhesive recommended by the manufacturer on the pipe as well as on sheet or preformed pipe section.

- Stick insulation slabs / pipe section of appropriate thickness with/ without pre-laminated aluminium foil (As specified in BOQ) on duct uniformly. Seal the joints with approved self-adhesive Aluminium tape. Flanges or any other exposed portion should be covered with 100 mm wide insulation slab of same material and thickness.

Indoor insulation shall be applied as follows (For Poly Iso Cynurate ):

- Clean the pipe surface thoroughly & apply a coat of adhesive recommended by the manufacturer on the pipe as well as on sheet or preformed pipe section.

- Poly Iso Cynurate having density of 33kg/m3 pipe insulation shall be carried out with preformed pipe sections. Adhesive should apply as per the manufactures manual. Pipe insulation shall be clad with 0.5mm aluminium sheet with 50mm overlapping joints. Cladding shall be tightly bonded to the insulated pipes with necessary grooves and held in position with 12mm no. 8 sheet metal screws.  The joints should be sealed with mastic sealants.

Outdoor Insulation (For EPS):

- Clean the pipe surface thoroughly & apply a coat of bituminous paint. Apply hot bitumen 80/25 @ 1.5 kg/sq. m on the surface and the inner side of insulation material.

- Stick insulation pipe sections having staggered joints & hold at 1000mm centre with 24G galvanized steel wire or PVC strapping & blind the surface with hot bitumen at 1.5 kg/sq. m. Seal the joints with approved sealant.

- Wrap 500 micron polythene sheet & seal with hot bitumen.

- Clad the duct with 0.5mm thick Al sheet with 50mm overlap and fixed with self-tapping no. 8 sheet metal screw and seal with mastic sealant.

Outdoor insulation shall be applied as follows (For Nitrile/Polyethylene):

- Clean the pipe surface thoroughly & apply a coat of adhesive recommended by the manufacturer on the pipe as well as on sheet.

- Stick insulation slabs / pipe section with/ without pre-laminated aluminium foil (as specified in BOQ) on duct uniformly.

- Seal the joints properly. Flanges or any other exposed portion should be covered with 100 mm wide insulation slab.

- If the insulation is without aluminium foil then clad the pipe with 0.5mm thick Al sheet with 50mm overlap and fixed with self-tapping no. 8 sheet metal screw and seal with mastic sealant.

Outdoor insulation shall be applied as follows (For Poly Iso Cynurate ):

- Clean the pipe surface thoroughly & apply a coat of adhesive recommended by the manufacturer on the pipe as well as on sheet or preformed pipe section.

- Poly Iso Cynurate having density of 33kg/m3 pipe insulation shall be carried out with preformed pipe sections. Adhesive for bonding sections shall be Foster Fire resistive adhesive 81-33 or as per the manufactures manual. Vapour seal like Foster Fire Retardant mastic 60-30 or equal shall be used.

- Pipe insulation shall be clad with 0.5mm aluminium sheet with 50mm overlapping joints. Cladding shall be tightly bonded to the insulated pipes with necessary grooves and held in position with 12mm no. 8 sheet metal screws.  The joints should be sealed with mastic sealants.

Underground Pipe Insulation:

- Clean the pipe surface thoroughly & apply a coat of bituminous paint.  Apply hot bitumen 80/25 @ 1.5 kg/sq. m on the surface and the inner side of insulation material.

- Stick insulation pipe sections having staggered joints & hold at 1000mm centre with 24G galvanized steel wire or PVC strapping & blind the surface with hot bitumen at 1.5 kg/sq. m. Seal the joints with approved sealant.

- Wrap 500 micron polythene sheet covered with 24G x 19mm G.I wire mesh tying with 20G GI lacing wire.

- Apply 2 layers of 6 mm thick sand cement plaster with water proofing compound. Cover the same with Tarfelt in such a way that the joints should be in bottom.

ii) Hot Insulation:

Hot pipe insulation shall be selected as follows:-

|  | Application | Thickness (mm) | Pipe (mm) dia. | Material |
| --- | --- | --- | --- | --- |
| a) | Hot water pipe not exceeding 50 deg. C | 50 50 | All sizes | Resin bonded fiberglass / Rockwool |
|  |  | 13 19 | Up to 80 mm Above 80 mm | Plain Nitrile rubber / Nitrile rubber with GC cloth |
| b) | Steam piping for saturated steam at less than 1 kg/scm (100 deg. C) | 25 38 | 12-40 50-150 | Resin bonded fibre glass or phenotherm |
| c) | Steam piping for saturated steam at 3 kg/scm (185° C) | 50 75 | 12-75 100 & Over | Unbonded Fibre glass |
| d) | Steam piping for saturated steam at 3 kg/sq.cm (145 ° C) | 75 | All sizes | Unbonded Fibre glass |
| e) | Thermic fluid at 250 ° C | 75 | “ | “ |

Resin bonded fibre glass shall be in pipe sections with reinforced aluminium foil face. The pipe shall be thoroughly cleaned with wire brush and the surface rendered free from rust. The cleaned surface shall be painted with one coat of bitumastic paint and the insulation applied with staggered joints. The insulation joints shall be sealed with adhesive tape and held in position with 1.0mm wire at 600 centres and finished with aluminium cladding of 0.5 mm.

Pipe including drain pipe insulation shall be clad with 0.5mm aluminium sheet with 50mm overlapping joints. Cladding shall be tightly bonded to the insulated pipes with necessary grooves and held in position with 12mm no. 8 sheet metal screws.  The joints should be sealed with mastic sealants.

  - Equipment Vessels & Tanks:

Kitchen hoods, Engine Exhaust pipes (if in scope) shall be insulated with 48 kg/cum unbounded fibre glass with galvanised wire netting on one side. The flue / pipe shall be thoroughly cleaned with wire brush to remove all mil scale and painted with one coat of bituminous paint. The wool blanket 100mm thick shall be applied with the wire netting on the outside. The insulation shall be held in position by lacing with 1.0mm dia. Galvanised steel wire and covered with fibre glass tissue with 75mm overlapping. The finished surface shall be clad with 0.50mm thick aluminium sheets with 50mm overlap and fixed with self-tapping No. 8 sheet metal screws.

Insulation of pumps for cold applications shall be the same as for the connected pipes. Insulation of pumps for hot application shall be the same as for connected pipes and application similar to cold application. The insulation shall be held in position with wire netting as above but shall not be covered with hot bitumen. Aluminium cladding of 24G shall be done over the insulation.

All vessels and tanks shall be insulated according to the connected pipe. All vessels & tanks shall be thoroughly cleaned with wire brush and rendered free of mil scale. Apply the surface with hot bitumen at 1.5 kg/sqm and stick the rigid insulation (in segments for cold insulation) holding it in position with 20mm x 0.63 mm galvanised wire mesh. Apply hot bitumen at 1.5 kg/sq.m over the finished surface and wrap it with 2mm tar felt with 50 mm over lapping. Retain the tar felt with 1mm galvanised steel wire and finish with 0.63 mm thick aluminium cladding.

  - Under Deck Roof Insulation:

Under-deck insulation shall be carried out using 12 mm thick fire retardant chemically cross linked polyethylene of 20 kg/m3. The surface shall be thoroughly cleaned with wire brush.  Apply factory recommended adhesives at spread rates recommended by the manufacturer on surface as well as on sheet and stick the sheet to the slab and allow it to cure. Screw the sheet in position with 0.63mm galvanized wire mesh. Hold the slabs in position such that the entire surface looks like one sheet. If the area is without false ceiling, then the insulation should be finished with 8 mm gypsum boards (by others).

  - Documentation

The vendor/ Contractor shall be responsible for preparing the following documents of all equipment’s in consultation with KCPL / Client.

- Design Qualification (DQ)

- Installation Qualification (IQ)

- Operational Qualification (OQ)

- Performance Qualification (PQ)

These documents shall be submitted as part of final documentation for handing over.

The following shall be submitted along with Quotations (in 2 sets):

- Technical Data sheet

- Enquiry document shall be duly filled, signed and stamped on all pages as an acceptance of the specifications.

- Deviation to the specification if any. Absence of list of deviations shall be construed as compliance of specifications in toto.

The following documents shall be submitted within 2 weeks of LOI/PO for Comments/Approval ( in 4 sets ):

- DQ document

- Typical Drawings along with sections.

- Purchase specifications for Bought-out components.

- Detailed Bar chart in MS Projects 2000.

- Quality assurance plan.

The following documents shall be submitted after installation (in 4 sets):

- PQ document

- Internal inspections & acceptance reports.

- Test & Guarantee certificates for all items.

- Material test certificates.

- DQ, IQ & OQ document.

  - Packing & Forwarding:

Material shall be dispatched to site with proper packing. It shall be covered with polyethylene sheets and it shall be insured that damage to the material does not occur during handling / transportation.

Vendor should consider the cost of packing and forwarding in the unit price of the material. No separate charges shall be paid for the same.

  - Mode of measurement:

- All duct insulation shall be measured on the basis of the duct prime surface area including insulation of flanges and excluding all openings for grilles, diffusers, dampers etc. In case of bends, tapers etc. the duct prime surface shall be determined on the basis of average dimensions.

- All pipe insulation shall be in linear measure along the centre line of the pipe over all fittings, excluding valves & strainers.  Insulation for valves with flanges will be included against individual values in BOQ.

- All pump and equipment insulation up to the flange be considered in the price of pump quoted in BOQ.

- All roof insulation and tank shall be based on the prime surface of the area to be insulated.

  - ABBREVIATIONS

| ASHRAE | : | American Society of Heating, Refrigerating and Air-Conditioning Engineers |
| --- | --- | --- |
| SMACNA | : | Air Movement and Control Association international Inc. |
| BOQ | : | Bill of quantity |
| DQ | : | Design Qualification |
| DW | : | General Arrangement |
| GI | : | Galvanised Iron |
| HVAC | : | Heating, Ventilation & Air Conditioning |
| ISO | : | International Organization for Standardization |
| KCPL | : | Knexir Consultant Pvt. Ltd. |
| OQ | : | Operational Qualification |
| PQ | : | Performance Qualification |
| IQ | : | Installation Qualification |
| URS | : | User Requirement Specification |